## Service Summary
| . | CPF50 |  | Multifamily (CPF50) EV Charging Site Validation
Rev: Dec 2019
Important: After performing this service and completing this checklist, you must:
1) Contact ChargePoint Support (877) 850-4562 before leaving the site to provide a status update.
2) Email this completed checklist to sitevalidation@chargepoint.com and mfactivations@chargepoint.com
Include in the subject line of the email ChargePoint ticket numbers for both Site Validation and Activation Services (see below).
Customer/Site Information
Company Name :
Site Address (list all):
City/State/Zip:
Site Contact Name(s):
Site Contact Phone #:
# of Total EV Make-Ready Spaces (includes panel capacity, conduit & all electrical wiring): |  |  |  | # of Total EV Capable Parking Spaces (panel capacity & conduit - excludes electrical wiring):
# of Total Resident Assigned Parking Spaces: |  |  |  | # of Total Parking Spaces (residents + guests)
# of Installed CPF50 Chargers: |  |  |  | Total # of EV Panels for CPF50:
# of Installed CP50 Gateway Devices: |  |  |  | # of 2-P 40A Breakers for CPF50:
# of Installed CT4000 Gateway Chargers: |  |  |  | # of EV Panels for CT4000:
Total # of Installed CT4000 Chargers (includes gateway): |  |  |  | # of 2-P 40A Breakers for CT4000:
Electrician Information
Electrical Company Name:
Electrician Name:
Electrician Phone #: |  |  |  | Electrician Email:
Assistant Name(s):
[5 empty] | Yes | No | Electrician License No.
You are a licensed electrician and an authorized Operations & Maintenance (O&M) ChargePoint parter. If not, you will be unable to complete the Site Validation process.
You have completed the ChargePoint online training modules specific to the CPF50 and CT4000 product family (http://chargepointuniversity.netexam.com/) to become a ChargePoint certified CPF50 installer and to get a ChargePoint login. If you have not completed this training, you will not be able to validate installation of the CPF50 product.
Service Details
Date of Service: |  |  |  | ChargePoint Site Validation Ticket #:
Arrival Time: |  |  |  | ChargePoint Activations Service Ticket #:
Departure Time: |  |  |  | Total Travel Hours:
Service Summary
|  |  | Yes | No | N/A
Issues noted during Site Validation:
Quote requested to remedy issues:
(double-click inside the box to view wrapped text)
Quote Details:

## Site Install Summary
Property Name:
Property Address:
Total number of installed CP Gateway Devices:
Total number of installed CPF50 installed stations/ports:
Radio Group Details | Gateway Device Mac Address | Measured Verizon 3G Signal* | Measured AT&T 3G Signal* | Total number of CPF50 stations/ports in this radio group (up to 9 CPF50s) | Garage or Bldg ID | Garage Floor Level (also include Stacked Parking Group # if applicable) | Describe location of installed Gateway Device installed (include nearest parking space #) | Gateway Device powered from EV Circuit feeding CPF50 (Yes/No). If Yes, include CPF50 MAC ID. If No, describe power source and voltage for gateway device, as well as breaker slot position. | Electric Panel Identifier and Panel Size (Amps per leg) | How many total 40A breakers at panel are deignated for EV charging? | Total Aggregate Power Available for EV Charging from this Panel (kVA) | Transformer Size (kVA) feeding EV Electrical Panel | Total Electrical Power Budget at Site for EV Charging (maximum ceiling kVA)
Radio Group #1 Gateway Device
Radio Group #2 Gateway Device
Radio Group #3 Gateway Device
Radio Group #4 Gateway Device
Radio Group #5 Gateway Device
Radio Group #6 Gateway Device
Radio Group #7 Gateway Device
Radio Group #1 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #1 CPF50 #1
Grp #1 CPF50 #2
Grp #1 CPF50 #3
Grp #1 CPF50 #4
Grp #1 CPF50 #5
Grp #1 CPF50 #6
Grp #1 CPF50 #7
Grp #1 CPF50 #8
Grp #1 CPF50 #9
Radio Group #2 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #2 CPF50 #1
Grp #2 CPF50 #2
Grp #2 CPF50 #3
Grp #2 CPF50 #4
Grp #2 CPF50 #5
Grp #2 CPF50 #6
Grp #2 CPF50 #7
Grp #2 CPF50 #8
Grp #2 CPF50 #9
Radio Group #3 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #3 CPF50 #1
Grp #3 CPF50 #2
Grp #3 CPF50 #3
Grp #3 CPF50 #4
Grp #3 CPF50 #5
Grp #3 CPF50 #6
Grp #3 CPF50 #7
Grp #3 CPF50 #8
Grp #3 CPF50 #9
Radio Group #4 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #4 CPF50 #1
Grp #4 CPF50 #2
Grp #4 CPF50 #3
Grp #4 CPF50 #4
Grp #4 CPF50 #5
Grp #4 CPF50 #6
Grp #4 CPF50 #7
Grp #4 CPF50 #8
Grp #4 CPF50 #9
Radio Group #5 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #5 CPF50 #1
Grp #5 CPF50 #2
Grp #5 CPF50 #3
Grp #5 CPF50 #4
Grp #5 CPF50 #5
Grp #5 CPF50 #6
Grp #5 CPF50 #7
Grp #5 CPF50 #8
Grp #5 CPF50 #9
Radio Group #6 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #6 CPF50 #1
Grp #6 CPF50 #2
Grp #6 CPF50 #3
Grp #6 CPF50 #4
Grp #6 CPF50 #5
Grp #6 CPF50 #6
Grp #6 CPF50 #7
Grp #6 CPF50 #8
Grp #6 CPF50 #9
Radio Group #7 - CPF50 Station Details | Station ID or MAC Address | Garage or Bldg ID | Parking Space # | Panel ID | Circuit ID (40A breaker slot positions) | Electrical Circuit Wiring Shared with other CPF50 units (daisy chain) - YES/NO? If yes, list IDs (last 4 alphanumeric characters of MAC address) for all CPF50 units that share the same circuit? | Is the Circuit ID clearly visible on the Junction Box or Disconnet for circuit feeding the CPF50 unit? Yes/No? | Is the Junction Box located in same parking space as CPF50? If not, describe location of junction box (or disconnect) relative to CPF50 unit. | Is the EV parking space # listed on the electrical panel schedule and associated with correct breaker slot positions? | Approximate distance of CPF50 to installed gateway unit and confirm within 150 feet line of sight.
Grp #7 CPF50 #1
Grp #7 CPF50 #2
Grp #7 CPF50 #3
Grp #7 CPF50 #4
Grp #7 CPF50 #5
Grp #7 CPF50 #6
Grp #7 CPF50 #7
Grp #7 CPF50 #8
Grp #7 CPF50 #9

## CPF50 Station(s) Evaluation
CPF50 Station Evaluation
Perform the following checks on each newly installed CPF50 personal charging station and place a checkmark in the appropriate field. Use the Comments section below to provide further details regarding any issues and use the Photos tab (the last tab) to upload pictures taken of those issues.
| CPF50 Station Checks | Yes | No | N/A
1 | You are a licensed electrician and an authorized Operations and Maintenance (O&M) ChargePoint parter. If not, you will be unable to complete the Site Validation process.
2 | Earth ground connection is made to the ground lugs (where applicable).
3 | All mounting hardware is tightly secured, and all stations are level and solid.
Service wiring has been fully inserted into the terminal block and all electrical connections are clean and snug.
4 | Electrical enclosures are clean and free of wire strands and metal shavings.
5 | All covers are installed and all fasteners are tightened.
6 | All CPF50 stations are within a 150-ft clear line-of-sight of their Gateway device.
7 | The LED located at the bottom of the ChargePoint Gateway is solid green (this may take up to 10 minutes).
A white light is displaying around the CPF50s connector dock and its WiFi LED, located on the left side of the main unit's cover, is solid green (this can take up to 10 minutes).
8 | The parking area is clean and free of all packaging and debris.
9 | The charging cables can fully extend and retract smoothly and properly (for CPF50 with Cable Management Kit).
10 | All pinpointing steps have been completed as described in the ChargePoint installation guide.
12 | The output cable wiring is properly installed. The small blue wire on the output cable is fully inserted into the connector on the terminal block. Wires are not laying parallel to the back face.
13 | Line-to-line voltage at all power plates measures 208/240 VAC.
14 | Line-to-ground voltage at all power plates measures 120 VAC and does not fall below 80 VAC under load.
Station Evaluation Comments
(double-click inside the box to view wrapped text)

## Breaker Panel & Transformer
Breaker Panel & Transformer Information
Perform the following checks on each breaker panel feeding each newly installed CPF50 station. Place a checkmark in the appropriate field. Use the Comments section below to provide further details regarding any issues and use the Photos tab (last tab) to upload pictures taken of those issues.
| Breaker Panel Checks | Yes | No | Value
1 | The breakers feeding each unit are two-pole, non-GFCI.
2 | The breakers feeding each unit are the correct quantity and size per the station configuration (50A in most cases and 20A in certain applications where panel capacity is limited). If 20A breakers are used, appropriate UL sticker on station must be verified.
3 | All 2P-40A breakers are new.
4 | The breaker slot positions at the panel are correctly labeled and cross referenced to the CPF50 parking space numbers.
5 | Site install summary completed with all information provided for each electrical panel.
6 | Site install summary completed and includes aggregate power ceiling for the site.
7 | Utility Service at this site includes the transformer feeding the Electrical Panel(s) used for EV charging.
8 | Transformer size in kVA load stated on transformer label. Record total kVA
9 | Transformer is dedicated exclusively for EV charging.
10 | Confirm only center-grounded systems were used (120/240 VAC, 1Ø bonded neutral, or 120/208 VAC, 3Ø WYE bonded neutral, or 120/240 VAC, 3Ø Delta center tap-grounded bonded neutral).
11 | Confirm the station is not connected to an ungrounded 120/208 VAC, 3Ø WYE, or a corner-grounded 120/240 VAC 3Ø Delta, or any system where the center point of the AC power source is not grounded.
Breaker Panel Evaluation Comments
(double-click inside the box to view wrapped text)

## Cellular Coverage Evaluation
Gateway Cellular Coverage Evaluation
Confirm the cellar network and signal strength (units of dbm) at each Gateway location. Enter this information into the Measured dbm Values column.
| GPRS (WCDMA on Squid) = AT&T 3G | CDMA (EVDO on Squid) = Verizon 3G
Using a Squid-Pro M2M cellular signal detector, confirm the cellular signal strength for both 3G AT&T (listed as WCDMA on Squid display) and 3G Verizon (listed as EVDO on Squid display) and enter this information into the Measured Values column.
Note: A measured signal value of less than -90 dbm (-100 dbm is less than -90 dbm) indicates poor cell coverage, and a signal booster should be recommended to the customer if both AT&T and Verizon carrier signal levels are unacceptable. If signal booster is determined necessary, identify outdoor and indoor antenna locations and document measured cell signal level at outdoor antenna location (ideal signal level of -65dbm or better to -80dbm on average). Note the weakest acceptable signal level at outside antenna location for signal booster to work properly is between -90 dbm to -100 dbm (the weaker the signal the less coverage area inside the parking garage using a signal booster). Also identify suitable location and power for the signal booster. Document locations of signal booster, indoor and outdoor antennas, and gateway devices in comment section below.
Measured dbm Values
| Parking Space & MAC Address |  | AT&T | Verizon
Gateway Station 1
Gateway Station 2
Gateway Station 3
Gateway Station 4
Gateway Station 5
Gateway Station 6
Gateway Station 7
Gateway Station 8
Gateway Station 9
Gateway Station 10
Gateway Cellular Coverage Evaluation Comments
(double-click inside the box to view wrapped text)

## Pinpoint Verification
Pinpoint Verification
Using the aerial images below, verify each station was correctly pinpointed during its activation.
Note: The below images will be provided by ChargePoint Support. Contact CPI Tech Support (877) 850-4562 while onsite if there are any issues with the station locations.
Aerial View 1
Provide Caption for Photo
Provide Caption for Photo
Aerial View 2
Provide Caption for Photo
Provide Caption for Photo
Aerial View 3
Provide Caption for Photo
Provide Caption for Photo
Aerial View 4
Provide Caption for Photo
Provide Caption for Photo
Aerial View 5
Provide Caption for Photo
Provide Caption for Photo

## Photos
Photos
Use this page to upload all photos taken onsite. Provide photo of each parking space with installed charging station, as well as each "EV make-ready" parking space without installed station. To upload a photo, right-click inside one of the boxes below and select "Change Picture". Then browse to the folder containing the photos, select a photo for inclusion, and provide an appropriate caption above the photo. There is no need to resize, separately email or upload these photos to another system.
Provide image of the installed station(s) | Provide Image of Open Electrical Panel | Provide Image of Concrete Pad(s)
Provide picture of wiring inside EVERY station | Provide Image of the Station Screen(s) | Provide Image of Other Installed Electrical Infrastructure
Proivde Image of Cellular Repearter (If applicable) | Photo inside the GW unit (modem) | Provide Caption for Photo
Provide Caption for Photo | Provide Caption for Photo | Provide Caption for Photo